## Summary
Category | TotalUndiv_A | Diversified_A
Lighting | 6.9565 | 4.5913
Socket-outlets | 35.087 | 24.5609
Cooking appliance | 13.0435 | 13.0435
Instantaneous water heater/shower | 0 | 0
Immersion (controlled) | 0 | 0
Immersion (uncontrolled) | 0 | 0
Fixed space heating | 0 | 0
EV charger | 0 | 0
Motors/pumps | 0 | 0
Other | 0.0086957 | 0.0086957
| Total Max Demand (A) | 42.2043

## Circuits
Circuit ID | Description | Category | Phase | Voltage | PowerFactor | RatedPower_W | RatedCurrent_A | CCU_Socket | UndivI_A | Notes
1 | Cooker | Cooking appliance | 1φ | 230 | 1 | 3000 |  | No | 13.0435 | Single Oven
2 | Smoke Alarms | Other | 1φ | 230 | 1 | 2 |  | No | 0.0086957 | House smokes
5 | Downstairs lights | Lighting | 1φ | 230 | 1 | 800 |  | No | 3.4783
6 | Upstairs Lights | Lighting | 1φ | 230 | 1 | 500 |  | No | 2.1739
11 | Downstairs Sockets | Socket-outlets | 1φ | 230 | 1 | 900 |  | No | 3.913 | Toaster
11 | Downstairs Sockets | Socket-outlets | 1φ | 230 | 1 | 3000 |  | No | 13.0435 | Kettle
11 | Downstairs Sockets | Socket-outlets | 1φ | 230 | 1 | 500 |  | No | 2.1739 | Coffee Machine
11 | Downstairs Sockets | Socket-outlets | 1φ | 230 | 1 | 150 |  | No | 0.65217 | Fridge
11 | Downstairs Sockets | Socket-outlets | 1φ | 230 | 1 | 900 |  | No | 3.913 | Dishwasher
11 | Downstairs Sockets |  | 1φ | 230 | 1 | 120 |  | No | 0.52174 | TV
12 | Upstairs Sockets | Socket-outlets | 1φ | 230 | 1 | 300 |  | No | 1.3043 | PC
12 | Upstairs Sockets | Socket-outlets | 1φ | 230 | 1 | 120 |  | No | 0.52174 | TV
15 | Garage | Socket-outlets | 1φ | 230 | 1 | 2200 |  | No | 9.5652 | Washing Machine
15 | Garage | Lighting | 1φ | 230 | 1 | 300 |  | No | 1.3043

## DiversityRules
Category | RuleType | Param1 | Param2 | Notes
Lighting | PercentOfTotal | 0.66 |  | Typical OSG domestic lighting diversity
Socket-outlets | LargestPlusRemainder | 1 | 0.4 | 100% largest + 40% remainder
Cooking appliance | CookerFormula |  |  | 10A + 30% remainder >10A + 5A if CCU socket
Instantaneous water heater/shower | PercentOfTotal | 1 |  | No diversity
Immersion (controlled) | PercentOfTotal | 0.5 |  | Off-peak/timed control
Immersion (uncontrolled) | PercentOfTotal | 1
Fixed space heating | LargestPlusRemainder | 1 | 0.75 | 100% largest + 75% remainder
EV charger | PercentOfTotal | 1 |  | No diversity unless load managed
Motors/pumps | PercentOfTotal | 1
Other | PercentOfTotal | 1

## Appliance Values
Appliance | Approx. Power (W) | Approx. Current (A @230 V) | Notes
Kettle | 2,200–3,000 | 9.5–13 | High load, short duration
Toaster (2-slice) | 900 | 4
Toaster (4-slice) | 2000 | 8.7
Microwave | 1500 | 6.5 | Standard model
Electric oven (single) | 3000 | 13 | Often on dedicated circuit
Hob (ceramic/induction) | 3,000–7,000 | 13–32 | May require diversity calc
Dishwasher | 2200 | 10
Washing machine | 2200 | 10
Tumble dryer (vented/condenser) | 2500 | 11
Tumble dryer (heat pump) | 800 | 3.5 | Energy-efficient type
Fridge freezer (standard) | 150 | 0.65 | Runs intermittently
American fridge freezer | 250 | 1.1
Freezer (upright/chest) | 100 | 0.4
Electric shower | 7,500–9,500 | 32–41 | Requires dedicated circuit
Immersion heater | 3000 | 13
Hair dryer | 2200 | 10
Iron | 3000 | 13
Fan heater / portable radiator | 2,000–3,000 | 9–13
Vacuum cleaner (corded) | 900–2,000 | 4–9
Cordless vacuum | 20–175 | <1 | Charging load
Laptop | 50–100 | <0.5
Desktop PC | 300 | 1.3 | Gaming rigs higher
TV (55” UHD) | 120 | 0.5
Games console | 200 | 0.86
EV charger (slow) | 3000 | 13 | Dedicated circuit
Smoke alarms | 1 |  | Dedicated circuit