## Circuits
Circuit ID | Description | Category | Phase | Voltage_V | PowerFactor | RatedPower_W | RatedCurrent_A | CCU_Socket | UndivI_A | RowDiversifiedI_A | Notes
1 | Cooker | Cooking appliance | 1φ | 230 | 1 |  |  |  | 0 | 0
2 | Upstairs lighting | Lighting | 1φ | 230 | 1 |  |  |  | 0 | 0
3 | Oven 3.5kW | Cooking appliance | 1φ | 230 | 1 | 3500 |  | Yes | 15.2174 | 16.5652
4 | Electric shower 9.5kW | Instantaneous water heater/shower | 1φ | 230 | 1 | 9500 |  |  | 41.3043 | 41.3043
5 | Panel heaters | Fixed space heating | 1φ | 230 | 1 | 2000 |  |  | 8.6957 | 8.6957 | (enter each heater as its own row)

## Sheet1
Appliance | Approx. Power (W) | Approx. Current (A @230 V) | Notes
Kettle | 2,200–3,000 | 9.5–13 | High load, short duration
Toaster (2-slice) | 900 | 4
Toaster (4-slice) | 2000 | 8.7
Microwave | 1500 | 6.5 | Standard model
Electric oven (single) | 3000 | 13 | Often on dedicated circuit
Hob (ceramic/induction) | 3,000–7,000 | 13–32 | May require diversity calc
Dishwasher | 2200 | 10
Washing machine | 2200 | 10
Tumble dryer (vented/condenser) | 2500 | 11
Tumble dryer (heat pump) | 800 | 3.5 | Energy-efficient type
Fridge freezer (standard) | 150 | 0.65 | Runs intermittently
American fridge freezer | 250 | 1.1
Freezer (upright/chest) | 100 | 0.4
Electric shower | 7,500–9,500 | 32–41 | Requires dedicated circuit
Immersion heater | 3000 | 13
Hair dryer | 2200 | 10
Iron | 3000 | 13
Fan heater / portable radiator | 2,000–3,000 | 9–13
Vacuum cleaner (corded) | 900–2,000 | 4–9
Cordless vacuum | 20–175 | <1 | Charging load
Laptop | 50–100 | <0.5
Desktop PC | 300 | 1.3 | Gaming rigs higher
TV (55” UHD) | 120 | 0.5
Games console | 200 | 0.86
EV charger (slow) | 3000 | 13 | Dedicated circuit

## DiversityRules
Category | Rule | Param1 | Param2 | Notes
Lighting | PercentOfTotal | 0.66 |  | Typical domestic lighting diversity per OSG
Socket-outlets (ring/radial) | LargestPlusRemainder | 1 | 0.4 | 100% largest circuit + 40% of remainder
Cooking appliance | CookerFormula |  |  | 10A + 30% of remainder over 10A + 5A if CCU socket
Instantaneous water heater/shower | PercentOfTotal | 1 |  | Electric shower/instantaneous heater usually 100%
Immersion heater (controlled) | PercentOfTotal | 0.5 |  | Storage heater on timer/off-peak
Immersion heater (uncontrolled) | PercentOfTotal | 1 |  | Uncontrolled storage heater
Fixed space heating | LargestPlusRemainder | 1 | 0.75 | 100% largest heater + 75% of remainder
EV charger | PercentOfTotal | 1 |  | Assume 100% unless load management limits apply
Motors/pumps | PercentOfTotal | 1 |  | e.g., CH pump, MVHR—typically 100%
Other | PercentOfTotal | 1 |  | Catch-all at 100%

## Summary
Category | Rule | Param1 | Param2 | TotalUndiv_A | Diversified_A
Lighting | PercentOfTotal | 0.66 | 0
Socket-outlets (ring/radial) | LargestPlusRemainder | 1 | 0.4
Cooking appliance | CookerFormula | 0 | 0
Instantaneous water heater/shower | PercentOfTotal | 1 | 0
Immersion heater (controlled) | PercentOfTotal | 0.5 | 0
Immersion heater (uncontrolled) | PercentOfTotal | 1 | 0
Fixed space heating | LargestPlusRemainder | 1 | 0.75
EV charger | PercentOfTotal | 1 | 0
Motors/pumps | PercentOfTotal | 1 | 0
Other | PercentOfTotal | 1 | 0
|  |  | Total Max Demand (A) | 0
|  |  | Approx. Max Demand (kVA) @230V | 0